## Sheet1
| Parameters | Values | Limit | Units
0 | Rating | 1.5 |  | MW
1 | Stator Arms | 5 |  | unit
2 | Stator Axial arm dimension | 213.4379 |  | mm
3 | Stator Circumferential arm dimension | 317.132 | 348.7168 | mm
4 | Stator arm Thickness | 96.2987 |  | mm
5 | Rotor Arms | 5 |  | unit
6 | Rotor Axial arm dimension | 336.634 |  | mm
7 | Rotor Circumferential arm dimension | 337.848 | 348.7168 | mm
8 | Rotor Arm thickness | 105.2982 |  | mm
9 | Rotor Radial deflection | 0.14937 | 0.20924 | mm
10 | Rotor Axial deflection | 0.2526 | 20.4976 | mm
11 | Rotor circum deflection | 1.7834 | 1.826 | mm
12 | Stator Radial deflection | 0.20245 | 0.23269 | mm
13 | Stator Axial deflection | 0.56548 | 20.4976 | mm
14 | Stator Circumferential deflection | 1.9311 | 2.0306 | mm
15 | Air gap diameter | 4.4698 |  | m
16 | Stator length | 1.0249 |  | m
17 | l/D ratio | 0.22929 | (0.2-0.27)
18 | Pole pitch | 158.3003
19 | Stator slot height | 67.5204 |  | mm
20 | Stator slot width | 11.9679 |  | mm
21 | Slot aspect ratio | 5.6418 | (4-10) | mm
22 | Stator tooth width | 14.6274 |  | mm
23 | Stator yoke height | 49.0211 |  | mm
24 | Rotor yoke height | 53.3927 |  | mm
25 | Rotor pole height | 110.8102 |  | mm
26 | Rotor pole width | 110.8102 |  | mm
27 | Average no load flux density | 0.62015 | (0.62-1.05) | T
28 | Peak air gap flux density | 0.70354 | 1.2 | T
29 | Peak stator yoke flux density | 0.72317 | 2 | T
30 | Peak rotor yoke flux density | 0.80161 | 2 | T
31 | Stator tooth flux density | 1.2034 | 2 | T
32 | Rotor pole core flux density | 1.3519 | 2 | T
33 | Pole pairs | 44 |  | -
34 | Generator output frequency | 15.0333 | (10-60) | Hz
35 | Generator output phase voltage(rms value) | 831.717 |  | V
36 | Generator Output phase current | 624.0806 |  | A
37 | Stator resistance | 0.048933 |  | om/phase
38 | Synchronous inductance | 0.013024 |  | p.u
39 | Stator slots | 528 |  | slots
40 | Stator turns | 176 |  | turns
41 | Stator conductor cross-section | 243.1769 |  | mm^2
42 | Stator Current density | 2.5664 | (3-6) | A/mm^2
43 | Specific current loading | 46.9316 | <60 | kA/m
44 | Field turns | 117 |  | turns
45 | Conductor cross-section | 24.9985 |  | mm^2
46 | Field Current | 29.9943 |  | A
47 | D.C Field resistance | 24.34 |  | ohm
48 | MMF ratio at rated load(Rotor/Stator) | 6.6012 |  | %
49 | Excitation Power (% of Rated Power) | 1.9996 | <2% | %
50 | Number of brushes/polarity | 1 |  | brushes
51 | Field Current density | 1.1998 | (3-6) | A/mm^2
52 | Generator Efficiency | 93.0091 | 93 | turns
53 | Iron mass | 20.9814 |  | %
54 | Copper mass | 8.4379 |  | tons
55 | Mass of Arms | 17.2036 |  | tons
56 | Total Mass | 46.623 |  | tons
57 | Total Cost | 60.6753 |  | 1000$