## Sheet1
| Parameters | Values | Limit | Units
0 | Rating | 5 |  | MW
1 | Stator Arms | 5 |  | unit
2 | Stator Axial arm dimension | 421.8726 |  | mm
3 | Stator Circumferential arm dimension | 536.6574 | 540.3539 | mm
4 | Stator arm Thickness | 43.6605 |  | mm
5 | Rotor Arms | 5 |  | unit
6 | Rotor Axial arm dimension | 552.3263 |  | mm
7 | Rotor Circumferential arm dimension | 528.1869 | 540.3539 | mm
8 | Rotor Arm thickness | 111.7013 |  | mm
9 | Rotor Radial deflection | 0.28902 | 0.3193 | mm
10 | Rotor Axial deflection | 0.47187 | 29.4728 | mm
11 | Rotor circum deflection | 2.3763 | 2.7864 | mm
12 | Stator Radial deflection | 0.33324 | 0.35418 | mm
13 | Stator Axial deflection | 0.85497 | 29.4728 | mm
14 | Stator Circumferential deflection | 2.992 | 3.0908 | mm
15 | Air gap diameter | 6.8119 |  | m
16 | Stator length | 1.4736 |  | m
17 | l/D ratio | 0.21633 | (0.2-0.27)
18 | Pole pitch | 200
19 | Stator slot height | 65.4556 |  | mm
20 | Stator slot width | 14.8613 |  | mm
21 | Slot aspect ratio | 4.4044 | (4-10) | mm
22 | Stator tooth width | 18.1638 |  | mm
23 | Stator yoke height | 140.8595 |  | mm
24 | Rotor yoke height | 132.2362 |  | mm
25 | Rotor pole height | 140 |  | mm
26 | Rotor pole width | 140 |  | mm
27 | Average no load flux density | 0.90463 | (0.62-1.05) | T
28 | Peak air gap flux density | 1.0263 | 1.2 | T
29 | Peak stator yoke flux density | 0.46383 | 2 | T
30 | Peak rotor yoke flux density | 0.60333 | 2 | T
31 | Stator tooth flux density | 1.7554 | 2 | T
32 | Rotor pole core flux density | 1.9945 | 2 | T
33 | Pole pairs | 54 |  | -
34 | Generator output frequency | 10.89 | (10-60) | Hz
35 | Generator output phase voltage(rms value) | 1903.9088 |  | V
36 | Generator Output phase current | 905.4736 |  | A
37 | Stator resistance | 0.069855 |  | om/phase
38 | Synchronous inductance | 0.0089991 |  | p.u
39 | Stator slots | 648 |  | slots
40 | Stator turns | 216 |  | turns
41 | Stator conductor cross-section | 291.9953 |  | mm^2
42 | Stator Current density | 3.101 | (3-6) | A/mm^2
43 | Specific current loading | 54.8355 | <60 | kA/m
44 | Field turns | 100 |  | turns
45 | Conductor cross-section | 46.0359 |  | mm^2
46 | Field Current | 68.9806 |  | A
47 | D.C Field resistance | 19.3029 |  | ohm
48 | MMF ratio at rated load(Rotor/Stator) | 3.8927 |  | %
49 | Excitation Power (% of Rated Power) | 1.3796 | <2% | %
50 | Number of brushes/polarity | 1 |  | brushes
51 | Field Current density | 1.4984 | (3-6) | A/mm^2
52 | Generator Efficiency | 93.1267 | 93 | turns
53 | Iron mass | 90.3127 |  | %
54 | Copper mass | 20.7583 |  | tons
55 | Mass of Arms | 38.4318 |  | tons
56 | Total Mass | 149.5029 |  | tons
57 | Total Cost | 168.8326 |  | 1000$